## Slide 1: Thermal Monitoring System
ECE 411 Practicum Project
By: Dmitriy Leonchik, Jose Aguliar, Mike Meza, and Rob Newcomb
December 11, 2014
Rev 6
Notes: Jose

## Slide 2: Problem
Busbars should be monitored for losses
Problems often go unmonitored
Cause $$$ in damages
Not many methods for doing this
Often too late to prevent damages
Can cause physical harm or death to personnel
Notes: Jose

## Slide 3: Busbars!
Busbar: Long metal conductor used to supply a steady flow of power to other electrical equipment. Often lamped, or welded connections, But most of the time bolted for maintenance If necessary.
Enclosure: These busbars are located in enclosures with limited visual appearance of the busbars themselves. Often there are simply no visual in the enclosure.

## Slide 4: Motivation
Detecting a fault on a busbar early can reduced downtime
Catch problem/over heating early stage
Prevent $$$ lost
Reduce effort to inspect dangerous busbar enclosure
Prevent harm to work personnel
Notes: Jose

## Slide 5: Objective
Design a system that will monitor the current and temperature of a busbar
System will be a prototype
System will only be functional for a small busbar system ( 12x5’’)
A small test jig will be used for demo purposes
Notes: Jose

## Slide 6: Busbar Damages

## Slide 7: Alternatives
IR gun sensor
  Requires personnel to manually measure temperature through sight glass
  Cannot reach all sections of busbar system
Thermal Imaging
  Requires personnel to manually measure temperature through sight glass
  Cannot reach all sections of busbar system
Notes: Jose

## Slide 8: Requirements
Product Design Specifications
Rev 5
System Should WORK!
Notes: Rob

## Slide 9: Approach
Research
    Thermal Sensors
    Microprocessors
    Current Transformers
    EagleCAD
    Displays
    Arduino IED
Test
    PCB Connections
    Each component separately
    Build system one component at a time
    System
Design
    Choose parts
    Draw Schematics
    Document
    Purchase Parts
Build
    ATMega 328P
    IR - MLX 90614
    CT – AL 101
    VR – 7805
    LCD – ST7066
Notes: Rob

## Slide 10: Design
Hardware
  CT
  IR
  LCD
  Rectifier
  Resistor bank
  Capacitors (10uF, 0.1uF)
  Resistors (47k, 10k)
  Voltage Regulator
Software
  Arduino IDE w/ Smart Cable
  IR code
  CT code
  LCD code
  Integration of all code
Notes: Mike

## Slide 11: Design- Activity View
Notes: Mike

## Slide 12: Design- CT Algorithm
Chart: CT: Current Vs. Voltage
| 30.9 | 38 | 46.8 | 53 | 60.4 | 66.099999999999994 | 70.2 | 77 | 80
mV | 32 | 104 | 252 | 380 | 516 | 650 | 708 | 852 | 916
Count Data | 1 | 16 | 45 | 69 | 97 | 121 | 137 | 167 | 180
Notes: Dima

## Slide 13: Design- Alternatives
Possible alternatives is link the PCB board to a PLC
Connect PLC to relays for a fault scenario
OR alternatives connected to a switch gear.
Integrate Possible program to integrate high current/temperature.
Measure torque of bolts.
Motion/vibration sensor
Fiber optic cable
Use Three Piece Enclosure
Notes: Dima

## Slide 14: Design - Trade-offs
Price
  Set budget of $200
Material
  Appearance
  Prototype only
Ease of Implementation
  Has to work with Test Jig
  Limited research needed for code
Notes: Dima

## Slide 15: Implementation
Major Components
  VR: 7805
  LCD: ST7066
  IR: MLX 90614
  CT: AL – 101
  Rectifier: VH848
Notes: Mike

## Slide 16: Implementation - Schematic
Notes: Mike

## Slide 17: Implementation – Board Layout
Notes: Mike

## Slide 18: Implementation- Code
Notes: Dima

## Slide 19: Implementation- Code Continued
Notes: Dima

## Slide 20: IP and Prior Work
Basic idea of system is a capstone project
Basic IR code obtained from http://bildr.org/?s=mlx90614
Took basic code to read temperature and modified it to work with out system
Idea came from DR. Bass for the project
Grad student is working on a PLC version for capstone we made a microcontroller prototype
Notes: Mike

## Slide 21: Testing
Functional Tests
  PCB
  Power and VR
  LCD
  IR
  CT
Microcontroller
  Power
  Blinking Light
  Hello World
  IR to LCD
  CT to LCD
  IR and CT to LCD
Component Tests
  IR
  CT
  LCD
Acceptance Test
  System Test
  Temperature Range
  Current Range
Notes: Rob

## Slide 22: Results
Power supply Pins backwords
Power source on PCB not grounded
Pin 28 not connected to SCL of IR
Pin 27 connected to CT instead of SDA of IR
Pin 26 not connected, should connect to CT
Pin 17 connected to IR, should be connected to E for LCD
Pin 16 connected to IR, should not be connected
Capacitors is series from Power
No capacitor for RESET
Notes: Rob

## Slide 23: Contributions
Prepare documentation – Rob
Review documentation – All Team members
Created GitHub account and uploaded documentation - Rob
Research microcontroller and test – Mike and Dmitriy
Research and test CT – Jose and Rob
Research and test IR – Dmitriy and Rob
Design layout – Mike
Design board layout – Mike

## Slide 24: Contributions
Research/wrote CT and IR code - Dmitriy
Write test plans – All team members
Design Enclosure – Jose
Build and Test prototype – Rob and Dmitriy
Build, Test, and assemble final product – All team members

## Slide 25: Lessons Learned
Better to have a PDS before Implementing a Project
Have WBS before starting project so it is clear what each team member needs to do and by when
Research each component thoroughly prior to working on a Project
Be open to design changes
Notes: Jose

## Slide 26: Lessons Learned
Have multiple people with overlapping skillsets
Have Design Reviews at all stages
Communication between members is key
Notes: Jose